SECTION 28 23 29

VIDEO SURVEILLANCE REMOTE DEVICES AND SENSORS

Advanced Technology Video HDV236 Vandal Dome Camera

******************************************

This guide specification is intended for use by the design/construction professional and any user of Advanced Technology Video (ATV) products to assist in developing project specifications for security and video surveillance systems.

Notes in Italics, such as this one, are explanatory and intended to guide the design professional/specifier and user in the proper selection and use of materials. This specification should be modified where necessary to accommodate individual project conditions.

******************************************

GENERAL

SUMMARY

Section includes Video Surveillance Remote Devices and Sensors.

Related Sections:

Section 28 23 13 – Video Surveillance Control and ManagementSystems

Section 28 23 16 – Video Surveillance Monitoring and SupervisoryInterfaces

Section 28 23 19 – Digital Video Recorders and Analog RecordingDevices

Section 28 23 23 – Video Surveillance Systems Infrastructure

SYSTEM DESCRIPTION

Description: Video surveillance and monitoring at points as indicated on Drawings.

HDV236: 2MP, True Day/Night, DWDR, HD Analog Vandal Dome Camera

Performance Requirements

Color camera using a 1/2.9” Sony CMOS sensor

HD Analog over Coax Technology: AHD & CVBS

Full HD, 1920 x 1080 resolution

TRUE Day/Night functionality

Smart IR LED Lights

IP66 rated weather resistant and IK10 impact resistant, metal dome housing enclosure

Digital Wide Dynamic Range

OSD Control via Coax cable using UTC

Long Distance, Real-Time, Transmission of Video over 1600ft on RG6U Coax Cable

The camera shall be of manufacturer’s official product line,designed for commercial/industrial continuous 24/7 use.

The camera shall be based upon standard components and proventechnology.

DEFINITIONS

TRUE Day/Night (infrared sensitive): A camera that has normal color operation in situations wherethere is sufficient illumination (day conditions), but where thesensitivity can be increased when there is little light available(night conditions). This is achieved by removing the infrared cutfilter required for good color rendition. The sensitivity can befurther enhanced by integrating a number of fields to improvethe signal-to-noise ratio of the camera (this may introducemotion blur).

Privacy Masking: The ability to mask out a specific area to prevent it from being viewed in order to comply with privacy laws and particular site requirements.

SUBMITTALS

Submit under provisions of Section 01 33 00 - Submittal procedures.

Shop Drawings: Indicate electrical characteristics and connection requirements, including system wiring diagram.

Product Data: Submit catalog data showing electrical characteristics and connection requirements for each component.

CLOSEOUT SUBMITTALS

Section 01 70 00 - Execution and Closeout Requirements: Closeout procedures.

Project Record Documents: Record actual locations of cameras and routing of cabling.

Operation and Maintenance Data: Submit instructions for operating system and performing routine trouble shooting procedures.

QUALIFICATIONS

Manufacturer: Company specializing in manufacturing products specified in this section with minimum ten years documented experience.

Supplier: Authorized distributor of specified manufacturer with minimum 5 years documented experience.

Installer: Authorized installer of specified manufacturer with 5 years documented experience  and with service

ENVIRONMENTAL REQUIREMENTS

Section 01 60 00 - Product Requirements.

Conform to manufacturer’s standard service conditions during and after installation of components.

FIELD MEASUREMENTS

Verify field measurements prior to fabrication.

MAINTENANCE SERVICE

Section 01 70 00 - Execution and Closeout Requirements: Maintenance service.

Furnish service and maintenance of video surveillance system for one year from Date of   Substantial Completion.

PRODUCTS

CAMERAS

Manufacturers:

Advanced Technology Video

Substitutions: Section01 60 00 - Product Requirements: Not Permitted.

Model: HDV236

Product Description: 2MP, True Day/Night, DWDR, HD Analog Vandal Dome Camera

Camera Image Sensor: 1/2.9” Sony Exmor CMOS

Lens: 3.6mm fixed lens

General Requirements:

Scene Illumination: 1.0Lux @F2.0, 50IRE; BW: 0Lux w/ IR LED On

Resolution: 1920 x 1080 Full HD

Signal to noise: more than 50dB (AGC off)

Scanning System: Progressive

True Day / Night with Infrared Cut Filter (ICR) removal function

Digital Wide Dynamic Range

Smart IR LED Lights

Camera Control: Joystick switch, Coaxial communication

Transmission Distance: Coax Cable, RG6U (5C-2V), 1640ft (500m); RG59 (3C-2V), 984ft (300m)

Video Requirements and Adjustments (minimum):

HD Analog over Coax Technology: AHD & CVBS

Video Mode: NTSC / PAL

Video Frame Rate: 1920 x 1080 (AHD) @ 25/30fps or 1000TVL (CVBS) @ 30fps

Effective Pixels: 2000(H) x 1121(V)

Day/Night:Auto (ICR)

Digital Wide Dynamic Range

White Balance

Auto Gain Control (AGC)

Back Light Compensation (BLC)

Shutter: 1/60 ~ 1/50,000 sec

Sens-UP

2DNR / 3DNR (Digital Noise Reduction

Digital Effects: Freeze, Mirror, Negative Image

Defect Detection

Language

Monitor

LSC (Shading)

Motion: 4 zones

Privacy: 4 zones

Brightness

Sharpness

Electrical:

Input Power: 12VDC +/- 10%.

Power Consumption:

360mA (4.3W)

Mechanical:

Vandal resistant, pre-packagedcast-aluminum housing: White color

Clear, polycarbonate dome bubble

Complete camera housing to be IP66 rated weather resistant and IK10 rated impact resistant

Power Input: 2.1mm barrel

Video Output: BNC Connector (AHD / CVBS selectable)

Smart IR LED Lights - 24 LED’s, 850nm; Distance: Maximum 82ft indoor, 62ft outdoor

Dimensions: 5.67Ø x 3.85in (144Ø x 98mm)

Weight: 1.17lbs (0.53kg)

Operating Temperature:  -22ºF ~ 140ºF (-30ºC ~ +60ºC)

Operating Humidity: 0 to 96% RH (non-condensing)

Conformity Certifications:

Federal Communications Commission (FCC)

European Conformity (CE)

NEMA-4X (IP66)

IEC (IK-10)

Underwriters Laboratories (UL)

Accessories

HDB243X: 	Wall Mount

HCS254V:	Flush Mount

HDA502:	Junction Box

HDB453:	Pendant Mount

HCM160:	Corner Mount

HDA401:	Wedge Mount

HPDA3:	Pendant Cap

Remote Management Software

Supported by ATVision IP Remote Management Client Software for Windows and Mac PC’s and Mobile Applications for Apple and Android Operating Systems

EXECUTION

EXISTING WORK

Disconnect and remove abandoned video surveillance equipment.

Extend existing video surveillance installations using materials and methods compatible with existing installations as specified.

Clean and repair existing video surveillance equipment remaining or to be reinstalled.

EXAMINATION

Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

Do not begin installation until unacceptable conditions are corrected.

PREPARATION

Protect devices from damage during construction.

INSTALLATION

Install devices in accordance with manufacturer’s instruction at locationsindicated on the floor drawings plans.

Perform installation with qualified service personnel.

Install devices in accordance with the National Electrical Code or applicablelocal codes.

Ensure selected location is secure and offers protection from accidentaldamage.

Ground and bond video surveillance equipment in accordance with Section 26 05 26.

Location must provide reasonable temperature and humidity conditions,free from sources of electrical and electromagnetic interference.

FIELD QUALITY CONTROL

Test snugness of mounting screws of all installed equipment.

Test proper operation of all video system devices.

Determine and report all problems to the manufacturer’s customer servicedepartment.

MANUFACTURER'S FIELD SERVICES

Section 01 40 00 - Quality Requirements:Manufacturer's field services.

Furnish manufacturer’s field representative to supervise final wiring connections and system adjustments.

ADJUSTING

Section 01 70 00 - Execution and Closeout Requirements: Requirements for starting and adjusting.

Make proper adjustment to video system devices for correct operation inaccordance with manufacturer’s instructions.

Make any adjustment of camera settings to comply with specific customer’s need.

Adjust manual lens irises to meet lighting conditions.

DEMONSTRATION AND TRAINING

Demonstrate at final inspection that video management system and devices function properly.

Demonstrate at final inspection camera’s functionality and video recording capabilities.

- END OF SECTION